Beam Plot

Mounting / Alignment

Mount the sensor so that the sensor face is parallel to the liquid or material surface and free of air currents.  Mount the sensor firmly to avoid vibration.

Wiring Connections, Connector Model

Accessories

Model	AC117		Sensor Cable - 5 meters (16 ft.)

Model 	AC226		Conveyor-Rail Clamp/Bracket Set

Model 	AC227		Mounting Bracket, Large (ACxxx Retrofit)

Model 	AC228		Mounting Bracket, Small

Mounting Bracket Dimensions

General Specifications

Power Supply:

Supply:	+12 to 24 VDC @ 50 mA max. (excluding output load)

Protection:	ESD and reverse-polarity

Sinking Output:

Maximum on-state voltage drop @ 100mA:	1.0 V

Maximum load current:	100 mA

Maximum applied voltage:	30 VDC

Protection:	ESD and over-current

Sourcing Output:

Maximum on-state voltage drop @ 200mA:	0.9 V

Maximum load current:	200 mA

Maximum output voltage:	Equal to supply voltage

Protection:	ESD and over-current

Response Time: 	5 mS on/ 5 mS off

Operating Temperature:

@ 12 VDC supply	0 to 60C (32F to 140F) @ 100% relative humidity

@ 24 VDC supply	0 to 50C (32F to 122F) @ 100% relative humidity

Sensing:

Fixed near alarm:	101.6 mm (4.00 in.)

Fixed far alarm:	127.0 mm (5.00 in.)

Fixed range:	254.0 mm (10.00 in.)

Limit edge accuracy:	 0.69 mm (0.027 in.)

Maximum plane-reflector angle:	 10

Sonic Cone Angle:	10 @ 50.8 mm (2.0 in.) total angle

Minimum object size (rod shape):	1.6 mm (0.06 in.) @ 38 mm (1.5 in.) distance

Sensor Dimensions:

Threads:	18 mm x 1 mm

Length:	64.7 mm (2.55 in.)

Sensor Cable Length:	3 Meters (10 Ft.) Standard

Sensor Materials:

Housing:	PEI

Transducer face:	FDA approved silicone rubber

Cable:	Non-toxic PVC jacket

LEDs:	Polycarbonate

Sensor Ratings and Approvals:

NEMA 4X (Indoor Use Only) 5, 12, 12K, 13, and IP67

Installation/Overvoltage Category:	II

CE Mark Compliant:	Declaration of conformity available upon request.

This Product is UL Listed if powered by a Class II Power Supply and protected by a 2.0A Max UL Listed Fuse

LIMITATIONS AND EXCLUSION OF WARRANTIES

All goods purchased from Hyde Park Electronics LLC shall be free from defects in materials, design and workmanship under normal conditions of use for one year from the date of shipment.  THIS WARRANTY IS THE SOLE WARRANTY AND IS EXPRESSLY IN LIEU OF ALL OTHER WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTY OF MERCHANTABILITY OF FITNESS FOR A PARTICULAR PURPOSE.  THE LIABILITY OF HYDE PARK TO ANY PURCHASER SHALL BE LIMITED EXCLUSIVELY TO THE COST OF REPLACEMENT OR REPAIR OF DEFECTIVE PARTS, AND SHALL NOT INCLUDE LIABILITY FOR ANY DIRECT, CONSEQUENTIAL OR INCIDENTAL DAMAGES WHATSOEVER, WHETHER FORESEEN OR UNFORESEEN, INCLUDING BUT NOT LIMITED TO LOST PROFITS, LOST SALES, OR INJURY TO PERSONS OR PROPERTY.

HYDE PARK ELECTRONICS LLC

1875 Founders Drive

Dayton, Ohio  45420-4017

Phone (937) 252-2121   Fax (937) 258-5830

Email: help@sesensors.com

Web Site: http://www.sesensors.com

 1997-2008 Hyde Park Electronics LLC

18 mm Diameter Dual Alarm Sensor

Near Alarm at 101.6 mm (4.00 in.), Far Alarm at 127.0 mm (5.00 in.)

Outputs Normally Closed. On loss of echo, Outputs are On

OPERATOR INSTRUCTIONS

SUPERPROX

SM602A-516-30

This Hyde Park self-contained, ultrasonic, dual alarm sensor is capable of sensing most objects within a fixed 31.8 to 254.0 mm (1.25 to 10.00 in.) sensing range (Fig.1).  Objects that are transparent, opaque, plastic, glass, metal, liquid or solid can be detected if located within the sensing range.

Near Limit

101.6 mm

(4.00 in.)

Far Limit

127.0 mm

(5.00 in.)

31.8 mm

(1.25 in.)

0.0 mm

(0.0 in.)

Range

254.0 mm

(10.00 in.)

Figure 1

Literature and application engineering assistance are provided by Hyde Park and its authorized distributors to aid the customer in selecting the product for an application.  The customer, however, is responsible for determining the suitability of the product in the application.