Beam Plot

Mounting / Alignment

Mount the sensor such that the reflective surface of the object to be detected is approximately centered within the sensor’s sensing window.  Mount the sensor firmly to avoid vibration.  For best results, the sensor face should be parallel to the liquid or material surface and free of air currents.

Wiring Connections, Connector Model

Indicator LEDs

Green LED:	ON when power is being supplied to sensor

Amber LED:	ON when object is detected within fixed window

Accessories

Model:	XXZAC117	Sensor Cable - 5 meters

Model 	XXZAC231	Mounting Bracket, Straight

Model 	XXZAC232	Mounting Bracket, S-Shaped

Mounting Bracket Dimensions

General Specifications

Power Supply:

Supply:	+12 to 24 VDC @ 70 mA max. (excluding output load)

Protection:	ESD and reverse-polarity

Sinking Output:

Maximum on-state voltage drop @ 100mA:	1.0 V

Maximum load current:	100 mA

Maximum applied voltage:	30 VDC

Protection:	ESD and over-current

Sourcing Output:

Maximum on-state voltage drop @ 200mA:	0.9 V

Maximum load current:	200 mA

Maximum output voltage:	Equal to supply voltage

Protection:	ESD and over-current

Response Time: 	500 uS on / 500 uS off

Operating Temperature:

@ 12 VDC supply	0 to 50C (32F to 122F) @ 100% relative humidity

@ 24 VDC supply	0 to 50C (32F to 140F) @ 100% relative humidity

Sensing:

Fixed window width:	3.2 mm (0.13 in.)

Fixed inner-window edge:	47.6 mm (1.88 in.)

Fixed outer-window edge:	50.8 mm (2.00 in.)

Window-edge accuracy:	 0.69 mm (0.027 in.)

Maximum plane-reflector angle:	 10

Sonic Cone Angle:	10 @ 50.8 mm (2.0 in.)  total angle

Minimum object width:	0.076 mm (0.003 in.) @ 44 mm (1.75 in.) distance

Minimum object size (rod shape):	0.127 mm (0.005 in.) @ 44 mm (1.75 in.) distance

Sensor Dimensions:

Threads:	18 mm x 1 mm

Length:	64.7 mm (2.55 in.)

Sensor Cable:	Model No.  AC117 - 5 meters (16 ft.)
			   (Must be purchased separately)

Sensor Materials:

Housing:	PEI

Transducer face:	FDA approved silicone rubber

Cable:	Non-toxic PVC jacket

LEDs:	Polycarbonate

Sensor Environmental Ratings:	NEMA 1, 3, 4x, 12, 13 and IP67

Installation/Overvoltage Category:	II

CE Mark Compliant:	Declaration of conformity available upon request.

LIMITATIONS AND EXCLUSION OF WARRANTIES

All goods purchased from Hyde Park Electronics LLC shall be free from defects in materials, design and workmanship under normal conditions of use for one year from the date of shipment.  THIS WARRANTY IS THE SOLE WARRANTY AND IS EXPRESSLY IN LIEU OF ALL OTHER WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTY OF MERCHANTABILITY OF FITNESS FOR A PARTICULAR PURPOSE.  THE LIABILITY OF HYDE PARK TO ANY PURCHASER SHALL BE LIMITED EXCLUSIVELY TO THE COST OF REPLACEMENT OR REPAIR OF DEFECTIVE PARTS, AND SHALL NOT INCLUDE LIABILITY FOR ANY DIRECT, CONSEQUENTIAL OR INCIDENTAL DAMAGES WHATSOEVER, WHETHER FORESEEN OR UNFORESEEN, INCLUDING BUT NOT LIMITED TO LOST PROFITS, LOST SALES, OR INJURY TO PERSONS OR PROPERTY.

HYDE PARK ELECTRONICS LLC

1875 Founders Drive

Dayton, Ohio  45420-4017

Phone (937) 252-2121   Fax (937) 258-5830

Email: help@sesensors.com

Web Site: http://www.sesensors.com

 1997-2006 Hyde Park Electronics LLC

XX3K1AU020KAM12

SUPERPROX

Flat Profile Small-Object Sensor

Fixed Sensing Window, 3.2 mm (0.13 in.) Wide

Window Located 47.6 to 50.8 mm (1.88 to 2.00 in.) from Sensor Face

OPERATOR INSTRUCTIONS

SUPERPROX

XX3K1AU020KAM12

This Hyde Park self-contained, ultrasonic, small-object sensor is capable of sensing most objects within a fixed 47.6 to 50.8 mm (1.88 to 2.00 in.) sensing range (Fig.1).  Objects that are transparent, opaque, plastic, glass, metal, liquid or solid can be detected if located within the sensing window. Objects as small as 0.127 mm (0.005 in.) diameter can be detected.

Near Limit

47.6 mm

(1.88 in.)

Far Limit

50.8 mm

(2.00 in.)

38.1 mm

(1.50 in.)

0.0 mm

(0.0 in.)

Figure 1

Literature and application engineering assistance is provided by Telemecanique and its authorized distributors to aid the customer in selecting the product for an application.  The customer, however, is responsible for determining the suitability of the product in the application.